## Slide 1: Network-Attack-Resilient Intrusion-Tolerant SCADA for the Power Grid
Amy Babay, Thomas Tantillo, Trevor Aron,
Marco Platania, and Yair Amir
Johns Hopkins University, AT&T Labs, Spread Concepts LLC

## Slide 2: Importance of SCADA Systems
Supervisory Control and Data Acquisition (SCADA) systems form the backbone of critical infrastructure services
  Power grid, water supply, waste management
To preserve control and monitoring capabilities, SCADA systems must be constantly available and run at their expected level of performance (able to react within 100-200ms)
SCADA system failures and downtime can cause catastrophic consequences, such as equipment damage, blackouts, and human casualties

## Slide 3: Basic SCADA Architecture
Substation
RTU
Physical
Equipment
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master
HMI
Control Center
LAN
…
Remote Terminal Units (RTUs) and Programmable Logic Controllers (PLCs): Control physical equipment in power substations
SCADA Master: Central control server, maintains current state of the system (based on updates from RTUs/PLCs) and issues supervisory commands
Human Machine Interface (HMI): provide graphical displays for operators to interact with the system

## Slide 4: Basic SCADA Architecture
Substation
RTU
Physical
Equipment
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master
HMI
Control Center
LAN
…
1
For illustration only – this is a very fragile architecture

## Slide 5: Modern SCADA Systems
SCADA Master Primary
SCADA Master Hot Standby
HMI
Substation
Cold-Backup Control Center
RTU
Physical
Equipment
LAN
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master Primary
SCADA Master Hot Standby
HMI
Primary Control Center
LAN
…
2-2
Modern systems add fault-tolerance

## Slide 6: Modern SCADA Systems
SCADA Master Primary
SCADA Master Hot Standby
HMI
Substation
Cold-Backup Control Center
RTU
Physical
Equipment
LAN
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master Primary
SCADA Master Hot Standby
HMI
Primary Control Center
LAN
…
2-2
Modern systems add fault-tolerance…but is it enough?

## Slide 7: Hostile Operating Environments
Traditional SCADA systems ran on proprietary networks
  Created air gap from outside world and attackers
Cost benefits and ubiquity of IP networks are driving SCADA to use IP networks
  Exposes SCADA to hostile environments, removing the air gap
Raises additional concerns because SCADA systems are:
  In service for decades
  Running legacy code with well-known exploits
  Increasingly becoming a target for attackers
Attacks: Stuxnet (2010), Ukraine (2015, 2016), and others…

## Slide 8: Hostile Environments
Fault tolerance is no longer sufficient
System-level attacks
  Compromised SCADA master can issue malicious control commands and manipulate monitoring information
  Hot-backup is not effective: compromised primary reports that it is working correctly
Network-level attacks
  Sophisticated attacks can take the primary control center offline at the time of the attacker’s choosing
  Cold-backup inherently incurs downtime (on the order of hours). Not effective when the attacker controls when downtime occurs and can force it to occur repeatedly
  Hot-backup introduces inconsistency due to “split-brain” problem

## Slide 9: Modern SCADA Systems
SCADA Master Primary
SCADA Master Hot Standby
HMI
Substation
Cold-Backup Control Center
RTU
Physical
Equipment
LAN
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master Primary
SCADA Master Hot Standby
HMI
Primary Control Center
LAN
…
2-2
Fault tolerance is not sufficient in hostile environments

## Slide 10: Modern SCADA Systems
SCADA Master Primary
SCADA Master Hot Standby
HMI
Substation
Cold-Backup Control Center
RTU
Physical
Equipment
LAN
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master Primary
SCADA Master Hot Standby
HMI
Primary Control Center
LAN
…
2-2
Fault tolerance is not sufficient in hostile environments

## Slide 11: Modern SCADA Systems
SCADA Master Primary
SCADA Master Hot Standby
HMI
Substation
Cold-Backup Control Center
RTU
Physical
Equipment
LAN
Wide-Area Network
Substation
PLC
Physical
Equipment
SCADA Master Primary
SCADA Master Hot Standby
HMI
Primary Control Center
LAN
…
2-2
Fault tolerance is not sufficient in hostile environments

## Slide 12: Our Contribution
The first SCADA architecture that simultaneously addresses system (SCADA master) compromises and network attacks
  Key idea: distributes SCADA master replicas across three or more active geographic sites to ensure continuous availability
An extension of the architecture that avoids constructing additional power company control centers by leveraging commodity data centers
  Makes the architecture feasible for deployment
An open-source implementation and evaluation of the architecture
  Spire: www.dsn.jhu.edu/spire

## Slide 13: Addressing System Compromises
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
  Prime protocol – latency guarantees under attack [ACKL11]
Notes: Amir, Y. and Coan, B. and Kirsch, J. and Lane, J.
IEEE Transactions on Dependable and Secure Computing (TDSC), 8(4), pages 564-577, July 2011.

## Slide 14: Addressing System Compromises
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
  Prime protocol – latency guarantees under attack [ACKL11]
What prevents an attacker from reusing the same exploit to compromise more than f replicas?

## Slide 15: Addressing System Compromises
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
  Prime protocol – latency guarantees under attack [ACKL11]
Diversity
  Present a different attack surface so that an adversary cannot exploit a single vulnerability to compromise all replicas
  Multicompiler from UC Irvine [HNLBF13]
Notes: Homescu, A. and Neisius, S. and Larsen, P. and Brunthaler, S. and Franz, M.
IEEE/ACM Int. Symp. Code Generation and Optimization (CGO) 2013
Profile-guided automated software diversity

## Slide 16: Addressing System Compromises
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
  Prime protocol – latency guarantees under attack [ACKL11]
Diversity
  Present a different attack surface so that an adversary cannot exploit a single vulnerability to compromise all replicas
  Multicompiler from UC Irvine [HNLBF13]
What prevents an attacker from compromising more than f replicas over time?

## Slide 17: Addressing System Compromises
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
  Prime protocol – latency guarantees under attack [ACKL11]
Diversity
  Present a different attack surface so that an adversary cannot exploit a single vulnerability to compromise all replicas
  Multicompiler from UC Irvine [HNLBF13]
Proactive Recovery
  Periodically rejuvenate replicas to a known good state to cleanse any potentially undetected intrusions
  3f+2k+1 replicas needed to simultaneously tolerate up to f intrusions and k recovering replicas [SBCNV10]
  2f+k+1 connected correct replicas required to make progress
Notes: P. Sousa, A. Bessani, M. Correia, N. F. Neves, and P. Verissimo, “Highly
available intrusion-tolerant services with proactive-reactive recovery,”
IEEE Trans. Parallel Distrib. Syst., vol. 21, no. 4, pp. 452–465, 2010.

## Slide 18: Intrusion Tolerance State-of-the-Art in Research
Substation
RTU
Physical
Equipment
Wide-Area Network
Substation
PLC
Physical
Equipment
A Single Control Center
SCADA
Master
HMI
SCADA
Master
SCADA
Master
SCADA
Master
SCADA
Master
SCADA
Master
LAN
…
6
3f+2k+1 = 6 total replicas
2f+k+1 = 4 connected correct replicas required to provide bounded delay
(progress: 4)

## Slide 19: Addressing Network Attacks (Part 1): Spines Intrusion-Tolerant Network
Resilient Overlay Network Architecture: overcomes compromises in the underlying network infrastructure
Intrusion-Tolerant Overlay Protocols: overcome compromises of overlay nodes
SJC
LAX
DEN
DFW
CHI
ATL
WAS
SVG
NYC
JHU
[IEEE ICDCS 2016]

## Slide 20: Addressing Network Attacks (Part 1): Spines Intrusion-Tolerant Network
Makes widespread network disruption nearly infeasible (requires simultaneous meltdown of multiple ISP backbones)
A dedicated (e.g. nation-state) attacker can still invest the resources to disconnect a single targeted site
Reduces the problem of addressing arbitrary network attacks to handling a single downed or disconnected site

## Slide 21: New Natural Extensions (1/2): Primary-Backup Sites with Intrusion-Tolerant Replication
Substation
RTU
Physical
Equipment
Spines Intrusion-Tolerant Network
Substation
PLC
Physical
Equipment
Cold-Backup Control Center
HMI
LAN
Primary Control Center
HMI
LAN
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
…
6-6

## Slide 22: New Natural Extensions (2/2): Active Intrusion-Tolerant Replication across Two Sites
Substation
RTU
Physical
Equipment
Spines Intrusion-Tolerant Network
Substation
PLC
Physical
Equipment
Control Center 1
HMI
LAN
SM
SM
SM
Control Center 2
HMI
LAN
SM
SM
SM
Need more than two sites to provide continuous availability!
…
3+3
(progress: 4)

## Slide 23: Addressing Network Attacks (Part 2): Active Replication Across Three or More Sites
Two sites (even if both active) cannot provide intrusion tolerance and the necessary resilience to network attacks
  True for any X + Y configuration
  Replication protocol requires more than half the replicas to work
  Site disconnection can make at least half of the system unavailable
  Therefore, a solution requires active replication across three or more sites
Control centers are expensive!
  Setup to control, monitor, and communicate with RTUs in the field
  Therefore, to be feasible, solutions should fit the two-control center model used by power companies
New idea: devise an architecture where additional sites beyond the two control centers do not need to control RTUs or PLCs
  Commodity data centers provide cost-effective alternative
  Commodity data centers are becoming prevalent

## Slide 24: Novel Resilient Configurations (1/6)
Substation
RTU
Physical
Equipment
Substation
PLC
Physical
Equipment
Control Center 1
HMI
SM
SM
Data Center 1
SM
SM
HMI
SM
SM
Spines
Spines
Two separate Spines networks:
One to communicate with RTUs in the field
One for SCADA Master coordination
Need to increase the number of replicas to cover disconnected sites due to network attacks!
Control Center 2
…
2+2+2
(progress: 4)

## Slide 25: Novel Resilient Configurations (2/6)
Substation
RTU
Physical
Equipment
Substation
PLC
Physical
Equipment
Control Center 1
Data Center 1
SM
SM
HMI
SM
SM
Spines
Spines
Control Center 2
SM
SM
SM
SM
SM
SM
SM
SM
HMI
Increase k to include the number of replicas in the largest site. In this case, k = 4.
…
4+4+4
(progress: 7)
3f+2k+1 = 3(1)+2(4)+1 = 12

## Slide 26: Novel Resilient Configurations (3/6)
Substation
RTU
Physical
Equipment
Substation
PLC
Physical
Equipment
Control Center 1
HMI
SM
SM
HMI
SM
SM
Spines
Spines
Control Center 2
Data Center 1
SM
SM
Data Center 3
SM
SM
Data Center 2
SM
SM
Increase k to include the size of largest site plus rejuvenating replica. In this case, k = 3.
3f+2k+1 = 3(1)+2(3)+1 = 10
2+2+2+2+2
(2 control centers)
(progress: 6)
…

## Slide 27: Novel Resilient Configurations (4/6)
Substation
RTU
Physical
Equipment
Substation
PLC
Physical
Equipment
Control Center 1
HMI
SM
SM
HMI
SM
SM
Spines
Spines
Control Center 2
Data Center 1
SM
SM
Data Center 3
SM
SM
Data Center 2
SM
SM
At least f+2 replicas in each control center ensures one correct replica that can control RTUs even with intrusion and ongoing rejuvenation in connected control site
SM
SM
…
First complete solution
3+3+2+2+2
(progress: 7)

## Slide 28: Novel Resilient Configurations (5/6)
Substation
RTU
Physical
Equipment
Substation
PLC
Physical
Equipment
HMI
SM
SM
Spines
Spines
Control Center 2
Data Center 1
SM
SM
SM
SM
SM
SM
SM
…
Complete solution for 3 total sites: (2 control centers, 1 data center)
6+6+6
SM
SM
SM
HMI
SM
SM
Control Center 1
SM
SM
SM
SM
(progress: 10)

## Slide 29: Novel Resilient Configurations (6/6)
Substation
RTU
Physical
Equipment
Substation
PLC
Physical
Equipment
Control Center 1
HMI
SM
SM
HMI
SM
SM
Spines
Spines
Control Center 2
Data Center 1
SM
SM
Data Center 2
SM
SM
SM
SM
SM
SM
…
Complete solution for 4 total sites: (2 control centers, 2 data centers)
Sweet-spot balancing the number of data center sites, the number of total replicas, and the communication overhead
3+3+3+3
(progress: 7)

## Slide 30: SCADA Architecture Comparison

## Slide 31: Intrusion-Tolerant SCADA Configuration Framework
General framework to create SCADA configurations that use S total sites (S > 2) and tolerate f intrusions
Minimum number of replicas required to overcome f intrusions, a single rejuvenating replica, and a single disconnected site, varying f and S (total number of sites).

## Slide 32: Putting it all Together: Complete SCADA System
Spire Software Architecture for Configuration 3+3+3+3

## Slide 33: Wide Area Update Latency Histogram
30-hour wide-area deployment of configuration 3+3+3+3
  Control centers at JHU and SVG, data centers at WAS and NYC
  10 emulated substations sending periodic updates
  1.08 million updates (108K from each substation)
  Nearly 99.999% of updates delivered within 100ms (56.5ms average)

## Slide 34: Wide Area Update Latency Plot
30-hour wide-area deployment of configuration 3+3+3+3
  Only 13 updates out of 1.08 million delivered with latency exceeding 100ms
  Only 1 update exceeded 200ms

## Slide 35: Wide Area: Latency Under Attack
Targeted attacks designed to disrupt the system
  All combinations of site disconnection (due to network attack) + proactive recovery

## Slide 36: Wide Area: Latency Under Attack
Targeted attacks designed to disrupt the system
  All combinations of intrusion + site disconnection (due to network attack) + proactive recovery

## Slide 37: The Spire Forum
Forum focused on open source intrusion-tolerant control systems for the power grid
Please join the Spire forum if interested
http://dsn.jhu.edu/spire
Distributed Systems and Networks Lab