## Slide 1: Spire: Cyberattack-resilient Power Grid Substations
Dr. Yair Amir
Department of Computer Science
Johns Hopkins University
yairamir@jhu.edu
Picture by
Notes: American public power association - https://www.publicpower.org/

## Slide 2: Increasing Cyber Attacks on Grid Control Systems Reinforce the Need for Intrusion-tolerant Systems…
Source: https://www.weforum.org/agenda/2019/03/hackers-are-causing-blackouts-it-s-time-to-boost-our-cyber-resilience/
Notes: World economic forum

## Slide 3: DoD Red Team Experiment (March – April 2017)
Hosted at Pacific Northwest National Lab
Sandia National Labs red team attacked NIST-compliant commercial SCADA architecture and Spire
Commercial system completely taken over
  MITM from enterprise network, direct PLC access within hours
Spire completely unaffected
  Even after providing access to replica + source code

## Slide 4: Hawaiian Electric Test Deployment (January – February 2018)
Spire test deployment at Hawaiian Electric
  “Mothballed” Honolulu plant
  Managed small power topology, controlling 3 physical breakers via a Modbus PLC
Outcome
  Operated continuously in a real environment for 6 days without interfering with plant systems
  Successfully met performance (latency) requirements
Babay, Amy, John Schultz, Thomas Tantillo, Samuel Beckley, Eamon Jordan, Kevin Ruddell, Kevin Jordan, and Yair Amir. "Deploying intrusion-tolerant SCADA for the power grid." In 2019 49th Annual IEEE/IFIP International Conference on Dependable Systems and Networks (DSN), pp. 328-335, 2019.

## Slide 5: Byzantine-resilient High-Voltage Relays in the Substation (2020 — 2023)
Department of Energy identified high-voltage transformers as the most vulnerable component of the grid
  Cost millions of dollars
  Long procurement process
  Compromising a few can impact the grid
High Voltage Protective Relays protect the transformers; Protective Relays may be vulnerable to cyberattacks
Byzantine-resilience: resilient all the way to intrusion-tolerance -- working correctly even after a successful intrusion by a sophisticated adversary
Source: https://www.electricaltechnology.org/2021/10/electric-power-distribution-network.html

## Slide 6: Physical Attacks on Substations in Ukraine
“Russia is systematically shelling electrical substations throughout Ukraine.”
source: https://texty.org.ua/articles/108414/whats-up-with-the-power-how-russia-destroys-energy-infrastructure/
Ukrenergo workers at a substation in eastern Ukraine are salvaging pieces of equipment that still can be used for repairs.
source: https://www.newyorker.com/culture/photo-booth/the-impact-of-russian-missile-strikes-on-ukraines-power-grid

## Slide 7: Physical Attacks on Substations in the US
“Attacks on Electrical Substations Raise Alarm.”
Sources:
https://www.nytimes.com/2023/02/04/us/electrical-substation-attacks-nc-wa.html
https://www.seattletimes.com/seattle-news/what-motivated-the-pacific-northwest-substation-attacks/
https://myfox8.com/news/investigations/power-grid-attack/2-months-since-moore-county/

## Slide 8: Byzantine-resilient High-Voltage Relays in the Substation (2020 — 2023)
The Cyberattack angle
A protective relay that does not trip when it should, can cause irreparable damage to the transformer and its connected customers
A protective relay that does unnecessarily trip, causes a major disruption to a large number of customers
DoE project addressing that angle
Collaboration between Pacific Northwest National Laboratory (PNNL), Sandia National Laboratories (SNL), and Johns Hopkins
Industry partners: GE, Siemens, and Hitachi Energy
Source: https://www.electricaltechnology.org/2021/10/electric-power-distribution-network.html

## Slide 9: Designing Byzantine-resilient Protection
Real-Time
Economic Factors
Long System Lifetime
Seamless System Integration
Very exact real-time latency requirement of quarter-power cycle in all operating conditions
The protective relay is a reasonably expensive device and there are many of them in the system
Resiliency with long system lifetime with continuous availability
The solution should be capable of integrating into existing substations without changes to the infrastructure

## Slide 10: Spire for the Substation
The first real-time Byzantine-resilient architecture and protocols for the substation that simultaneously address system compromises and network attacks while meeting the strict timeliness requirement (4.167ms)
Bommareddy, Sahiti, Daniel Qian, Christopher Bonebrake, Paul Skare, and Yair Amir.
“Real-time byzantine resilience for power grid substations.”
In 2022 41st International Symposium on Reliable Distributed Systems (SRDS), pp. 213-224. IEEE, 2022.
Sahiti Bommareddy, Maher Khan, David J Sebastian Cardenas, Carl Miller, Christopher Bonebrake, Yair Amir and Amy Babay.
“Real-Time Byzantine Resilient Power Grid Infrastructure: Evaluation and Trade-offs”.
In International Workshop on Explainability of Real-time Systems and their Analysis at the IEEE Real-Time Systems Symposium (RTSS 2022).
Hitachi
Energy
GE
Siemens

## Slide 11: Toward a Byzantine-resilient Architecture
Protective Relay
Protective Relay
Protective Relay
Malicious Relay
f=1
f+1 relays need to agree on an action
f+1=2

## Slide 12: Toward a Byzantine-resilient Architecture
Protective Relay
Protective Relay
Protective Relay
Malicious Relay
f=1
f+1 relays need to agree on an action
f+1=2
Protective Relay
Relay for proactive recovery
k=1

## Slide 13: Typical IEC61850 Substation Architecture
Measured
Data
(Sampled Values)
Protective Relay
Protective Relay
Circuit Breaker
IED

## Slide 14: Byzantine-resilient Substation Architecture
Measured
Data
(Sampled Values)
Circuit Breaker
IED
Breaker
Proxy
Protective Relay
Relay
Proxy
Trip
Master
Protective Relay
Relay
Proxy
Trip
Master
Protective Relay
Relay
Proxy
Trip
Master
Protective Relay
Relay
Proxy
Trip
Master

## Slide 15: Protocol: State Machine

## Slide 16: Evaluation Operating Conditions
Operation Condition | Explanation
Fault-Free (Normal) | All four relay nodes are working correctly
Fail-Stop Fault or Proactive Recovery | One of the relay nodes is unavailable due to a fail-stop fault or proactive recovery
Fail-Stop Fault and Proactive Recovery | One of the relay nodes is unavailable due to a fail-stop fault while simultaneously, an additional relay node is undergoing proactive recovery
Byzantine Fault | One of the relay nodes is under the control of a sophisticated attacker. Such compromised node performs two simultaneous attacks for each action : send corrupt share and short intermittent denial of service attacks
Byzantine Fault and Proactive Recovery | One of the relay nodes exhibits the Byzantine Fault condition described above, and simultaneously, an additional relay node is undergoing proactive recovery

## Slide 17: Performance Evaluation : Fault-free Operating Condition
Latency in microseconds
Million Actions
Minimum / Average / Maximum
1604 / 2048 / 2789 microseconds

## Slide 18: Performance Evaluation : Fail-Stop Fault or Proactive Recovery Operating Condition
Latency in microseconds
Million Actions
Minimum / Average / Maximum
1604 / 2132 / 3135 microseconds

## Slide 19: Performance Evaluation : Byzantine Fault Operating Condition
Latency in microseconds
Million Actions
Minimum / Average / Maximum
1716 / 2268 / 3253 microseconds

## Slide 20: Performance Evaluation : Byzantine Fault and Proactive Recovery Operating Condition
Latency in microseconds
Million Actions
Minimum / Average / Maximum
1733 / 2261 / 5028 microseconds

## Slide 21: Performance Evaluation : Fail-Stop Fault and Proactive Recovery Operating Condition
Latency in microseconds
Million Actions
Minimum / Average / Maximum
1595 / 2167 / 5025 microseconds

## Slide 22: Real-Time Kernel Option
With only two nodes available, a random delay on either node (e.g., from network delays, kernel scheduling, or even effects of a Byzantine node’s actions) would be reflected in the end-to-end latency
Real-time kernel is optimized to maintain low-latency consistent response time and determinism
The determinism and latency stability of real-time kernel help to always meet the real-time requirement in all operating conditions
Sahiti Bommareddy, Maher Khan, David J Sebastian Cardenas, Carl Miller, Christopher Bonebrake, Yair Amir and Amy Babay.
“Real-Time Byzantine Resilient Power Grid Infrastructure: Evaluation and Trade-offs”.
In International Workshop on Explainability of Real-time Systems and their Analysis at the IEEE Real-Time Systems Symposium (RTSS 2022).

## Slide 23: Machine Learning-based Situational Awareness
We use machine learning-based intrusion detection
  Unsupervised Models
  Bag of Models
  Out-of-Band Detection
  Two levels of Modules: Network-level and Power system-level
Network level Module
  Packet Analysis-based Models
  Traffic Flow-based Models
Power systems level module

## Slide 24: Spire for the Substation
The first real-time Byzantine resilient architecture and protocols for the substation that simultaneously address system compromises and network attacks while meeting the strict timeliness requirement (4.167ms)
Successful red team experiment in 2022 (Sandia National Laboratories @ PNNL)
Industry Transition (GE 12/2022, Siemens 1/2023, perhaps Hitachi Energy)
Johns Hopkins open-source release: Spire 2.0 (www.dsn.jhu.edu/spire)
Bommareddy, Sahiti, Daniel Qian, Christopher Bonebrake, Paul Skare, and Yair Amir.
“Real-time byzantine resilience for power grid substations.”
In 2022 41st International Symposium on Reliable Distributed Systems (SRDS), pp. 213-224. IEEE, 2022.
Sahiti Bommareddy, Maher Khan, David J Sebastian Cardenas, Carl Miller, Christopher Bonebrake, Yair Amir and Amy Babay.
“Real-Time Byzantine Resilient Power Grid Infrastructure: Evaluation and Trade-offs”.
In International Workshop on Explainability of Real-time Systems and their Analysis at the IEEE Real-Time Systems Symposium (RTSS 2022).

## Slide 25: Questions / Comments
www.dsn.jhu.edu/spire
yairamir@jhu.edu

## Slide 26: Backup Slide 1
Substation

## Slide 27: Backup Slide 2

## Slide 28
28
Closed
(close, close)
Attempt Close
(close, trip)
r.t ≧ b.t
Tripped
(trip, trip)
Attempt Trip
(trip, close)
r.t ≧ b.t
Local Relay Trip
Local Relay Trip /
Trip Share Timeout
Trip Share
Combine Success
Or
Signed Trip Ack
Local Relay Close
Close Share
Combine Success
Or
Signed Close Ack
Local Relay Close
Local Relay Trip
Local Close Trip /
Close Share Timeout
Wait Trip
(close, trip)
r.t < b.t
Wait Close
(trip, close)
r.t < b.t
Signed
Trip Ack
Local Relay Trip
Signed
Close Ack
Local Relay Close
Signed
Close Ack
Signed
Trip Ack
Signed
Close Ack
Signed
Trip Ack
Local Relay Close
Or
Signed Close Ack
Local Relay Trip
Or
Signed Trip Ack
Signed Close Ack
r.t >= b.t
Local Relay
Close
Local Relay
Trip
Signed
Trip Ack
Signed
Close Ack
state=(relay, breaker)
STATE MACHINE