## Slide 1: Spire: Intrusion-Tolerant SCADA for the Power Grid
Yair Amir, Amy Babay, Sam Beckley
Johns Hopkins University, Computer Science
John Schultz
Spread Concepts LLC

## Slide 2: SCADA Migrating to IP Networks
Traditional SCADA systems ran on proprietary networks
  Created air gap from outside world and attackers
Cost benefits and ubiquity of IP networks are driving SCADA to use IP networks
  Exposes SCADA to hostile environments, removing the air gap
Raises additional concerns because SCADA systems are:
  In service for decades
  Running legacy code with well-known exploits
  Increasingly becoming a target for attackers
Stuxnet (2010)
  First sophisticated SCADA attack in the wild targeting ICS

## Slide 3: SCADA is Vulnerable on Several Fronts
The move to IP makes SCADA vulnerable on several fronts:
SCADA system compromises
  SCADA Master – system-wide damage
  RTUs, PLCs – limited local effects
  HMIs
Network level attacks
  Routing attacks that disrupt or delay communication
  Isolating critical components from the rest of the network
PLC
Physical
Equipment
RTU
Physical
Equipment
HMI
Primary
SCADA Master
Backup
SCADA Master

## Slide 4: Spire
Spire is an intrusion-tolerant SCADA system for the power grid: it continues to work even if some critical components have been compromised
Intrusion tolerance as the core design principle:
  Intrusion-tolerant network
  Intrusion-tolerant consistent state
  Intrusion-tolerant SCADA Master
Open Source - http://dsn.jhu.edu/spire

## Slide 5: DoD ESTCP Results
NIST-compliant system completely taken over
  MITM attack from corporate network
  Direct access to PLC from operational network
Spire completely unaffected
  Attacks in corporate and operational network
  Given complete access to a replica and code
  Red team gave up after several days

## Slide 6: Defense Across Space and Time
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress

## Slide 7: Defense Across Space and Time
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
What prevents an attacker from reusing the same exploit to compromise more than f replicas?

## Slide 8: Defense Across Space and Time
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
Diversity
  Present a different attack surface so that an adversary cannot exploit a single vulnerability to compromise all replicas
  Multicompiler from UC Irvine

## Slide 9: Defense Across Space and Time
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
Diversity
  Present a different attack surface so that an adversary cannot exploit a single vulnerability to compromise all replicas
  Multicompiler from UC Irvine
What prevents an attacker from compromising more than f replicas over time?

## Slide 10: Defense Across Space and Time
Byzantine Fault Tolerant Replication (BFT)
  Correctly maintains state in the presence of compromises
  3f+1 replicas needed to tolerate up to f intrusions
  2f+1 connected correct replicas required to make progress
Diversity
  Present a different attack surface so that an adversary cannot exploit a single vulnerability to compromise all replicas
  Multicompiler from UC Irvine
Proactive Recovery
  Periodically rejuvenate replicas to a known good state to cleanse any potentially undetected intrusions
  3f+2k+1 replicas needed to simultaneously tolerate up to f intrusions and k recovering replicas
  2f+k+1 connected correct replicas required to make progress

## Slide 11: Spire Architecture: Single Control Center

## Slide 12: Beyond a Single Site
To protect against sophisticated network attacks, Spire supports multiple control sites
Since it is expensive to construct control sites, Spire is able to operate with two control sites plus additional sites that can be served by commodity data centers (that lack the ability to communicate with RTUs and PLCs in the field)

## Slide 13: Novel Resilient Configuration
Substation
RTU
Physical
Equipment
Substation
RTU
Physical
Equipment
Control Center 1
HMI
SM
SM
HMI
SM
SM
Spines
Spines
Control Center 2
Data Center 1
SM
SM
Data Center 2
SM
SM
SM
SM
SM
SM
…
3+3+3+3
(progress: 7)

## Slide 14: Wide Area Update Latency Plot
30-hour wide-area deployment of configuration 3+3+3+3
  Control centers at JHU and SVG, data centers at WAS and NYC
  10 emulated substations sending periodic updates
  1.08 million updates (108K from each substation)
  Nearly 99.999% of updates delivered within 100ms (56.5ms average)

## Slide 15: Wide Area: Latency Under Attack
Targeted attacks designed to disrupt the system
  All combinations of site disconnection (due to network attack) + proactive recovery

## Slide 16: Wide Area: Latency Under Attack
Targeted attacks designed to disrupt the system
  All combinations of intrusion + site disconnection (due to network attack) + proactive recovery

## Slide 17: The Spire Forum
Forum focused on open source intrusion-tolerant control systems for the power grid
Please join the Spire forum if interested
http://dsn.jhu.edu/spire
Distributed Systems and Networks Lab